## Pipes
pipe # | start | end | pipe type | nominal dia | id (mm) | length (m) | static head (endZ-startZ) | flow | consumption | minimum pressure required | velocity | head loss | total head loss | Pressure at end of pipe | start with | end with | costs per meter | total costs
Pipe 1 | (536.08593755699, 1927.8727861776483, -5.0) | (1112.7556223528027, 2005.6658755842977, 12.456795843159185) | PE100-16 | 800 | 654.8 | 582.155 | 17.4568 | 1900 | 500 | 0 | 1.5673 | 1.8251 | 19.4071 | 85.2127 | Pump 1 | Pipe 2 | 3684.0206 | 2144670.9506
Pipe 2 | (1112.7556223528027, 2005.6658755842977, 12.456795843159185) | (375.6218616416263, 3051.911036071446, 3.0) | Steel | 20 | 484 | 1279.8768 | -9.4568 | 1400 | 0 | 0 | 2.1137 | 9.9321 | 0.70308 | 84.5096 | Pipe 1 | Pipe 3, Pipe 6 | 1140 | 1459059.5185
Pipe 3 | (375.6218616416263, 3051.911036071446, 3.0) | (144.03445550263132, 2923.579361220609, 5.0) | PE100-10 | 500 | 440.6 | 264.7749 | 2 | 1100 | 300 | 70 | 2.0041 | 2.0772 | 4.282 | 80.2276 | Pipe 2 | Pipe 4 | 1200 | 317729.875
Pipe 4 | (144.03445550263132, 2923.579361220609, 5.0) | (-945.1143240436759, 3200.8674386767834, 10.0) | PE100-12.5 | 315 | 268.6 | 1123.9034 | 5 | 800 | 500 | 20 | 3.9218 | 54.4434 | 60.2276 | 20 | Pipe 3 | Pipe 5 | 640 | 719298.1445
Pipe 5 | (-945.1143240436759, 3200.8674386767834, 10.0) | (-1100.785987141615, 3568.9949130421483, 0.0) | Steel | 10 | 253 | 399.8143 | -10 | 300 | 300 | 0 | 1.6576 | 4.2143 | -5.6456 | 25.6456 | Pipe 4 |  | 520 | 207903.4552
Pipe 6 | (375.6218616416263, 3051.911036071446, 3.0) | (1370.9059072682867, 3714.0837835015136, 10.0) | Steel | 16 | 382 | 1195.4548 | 7 | 300 | 200 | 0 | 0.72711 | 1.6942 | 8.7211 | 16.9244 | Pipe 2 | Pipe 7 | 830 | 992227.4493
Pipe 7 | (1370.9059072682867, 3714.0837835015136, 10.0) | (705.2600463000927, 4199.2185612304365, 10.0) | PE100-16 | 225 | 184 | 823.6748 | 0 | 100 | 100 | 0 | 1.0447 | 5.3522 | 5.4078 | 11.5166 | Pipe 6 |  | 442 | 364064.2585

## Pumps
pump # | center | flow | head | efficiency | start num | power | wetpit min volume | connect to pipe
Pump 1 | (536.08593755699, 1927.8727861776483, -5.0) | 1900 | 104.6198 | 0.75 | 8 | 721.7777 | 59.375 | Pipe 1

## eco Pipes
pipe # | start | end | pipe type | nominal dia | id (mm) | length (m) | static head (endZ-startZ) | flow | consumption | minimum pressure required | velocity | head loss | total head loss | Pressure at end of pipe | start with | end with | costs per meter | total costs
Pipe 1 | (536.08593755699, 1927.8727861776483, -5.0) | (1112.7556223528027, 2005.6658755842977, 12.456795843159185) | PE100-16 | 710 | 581 | 582.155 | 17.4568 | 1900 | 500 | 0 | 1.9907 | 3.2673 | 20.9262 | 76.4824 | Pump 1 | Pipe 2 | 2650 | 1542710.7177
Pipe 2 | (1112.7556223528027, 2005.6658755842977, 12.456795843159185) | (375.6218616416263, 3051.911036071446, 3.0) | Steel | 20 | 484 | 1279.8768 | -9.4568 | 1400 | 0 | 0 | 2.1137 | 9.9321 | 0.70308 | 75.7793 | Pipe 1 | Pipe 3, Pipe 6 | 1140 | 1459059.5185
Pipe 3 | (375.6218616416263, 3051.911036071446, 3.0) | (144.03445550263132, 2923.579361220609, 5.0) | PE100-10 | 450 | 396.6 | 264.7749 | 2 | 1100 | 300 | 70 | 2.4734 | 3.4674 | 5.7793 | 70 | Pipe 2 | Pipe 4 | 1010 | 267422.6448
Pipe 4 | (144.03445550263132, 2923.579361220609, 5.0) | (-945.1143240436759, 3200.8674386767834, 10.0) | PE100-12.5 | 400 | 341.2 | 1123.9034 | 5 | 800 | 500 | 20 | 2.4304 | 16.98 | 22.2812 | 47.7188 | Pipe 3 | Pipe 5 | 956 | 1074451.6033
Pipe 5 | (-945.1143240436759, 3200.8674386767834, 10.0) | (-1100.785987141615, 3568.9949130421483, 0.0) | Steel | 10 | 253 | 399.8143 | -10 | 300 | 300 | 0 | 1.6576 | 4.2143 | -5.6456 | 53.3644 | Pipe 4 |  | 520 | 207903.4552
Pipe 6 | (375.6218616416263, 3051.911036071446, 3.0) | (1370.9059072682867, 3714.0837835015136, 10.0) | Steel | 10 | 253 | 1195.4548 | 7 | 300 | 200 | 0 | 1.6576 | 12.601 | 19.7411 | 33.6233 | Pipe 2 | Pipe 7 | 520 | 621636.4743
Pipe 7 | (1370.9059072682867, 3714.0837835015136, 10.0) | (705.2600463000927, 4199.2185612304365, 10.0) | PE100-16 | 160 | 130.8 | 823.6748 | 0 | 100 | 100 | 0 | 2.0672 | 28.2043 | 28.4222 | 5.2011 | Pipe 6 |  | 257 | 211684.4218

## eco Pumps
pump # | center | flow | head | efficiency | start num | power | wetpit min volume | connect to pipe
Pump 1 | (536.08593755699, 1927.8727861776483, -5.0) | 1900 | 97.4086 | 0.75 | 8 | 672.0271 | 59.375 | Pipe 1

## Channels
channel # | start | end | length (m) | static head (endZ-startZ) | slope | manning coeficent | flow | velocity | water depth | max flow rates | max water depth | geometry: bottom width | geometry: bank slope | geometry: channel depth | geometry: channel width | geometry: free board | start with | end with
Channel 1 | (-341.40441576579906, 4449.161529270728, 10.0) | (927.8443495684223, 3180.6366404926175, 0.0) | 1794.5049 | 10 | 0.0055726 | 0.035 | 1200 | 0.68129 | 0.27008 |  | 0 | 1 | 3 |  |  | 0.25
Channel 2 | (927.8443495684223, 3180.6366404926175, 0.0) | (1727.2269999314958, 2747.6305526536253, -10.0) | 909.1792 | 10 | 0.010999 | 0.035 | 1200 | 0.90546 | 0.35019 | 793.8683 | 0.3 | 0 | 3 |  |  | 0.25
Channel 3 | (1727.2269999314958, 2747.6305526536253, -10.0) | (2380.157882571122, 2375.611237107036, -20.0) | 751.5432 | 10 | 0.013306 | 0.035 | 1200 | 0.93542 | 0.17815 | 13957.3754 | 0.95 | 2 | 0 | 1.2 |  | 0.25