## Pipes
pipe # | start | end | pipe type | nominal dia | id (mm) | length (m) | static head (endZ-startZ) | flow | consumption | minimum pressure required | velocity | head loss | total head loss | Pressure at end of pipe | start with | end with | costs per meter | total costs
Pipe 1 | (536.08593755699, 1927.8727861776483, -5.0) | (1031.5975623507745, 1994.7176041834116, 10.0) | PE100-16 | 800 | 654.8 | 500.2249 | 15 | 2400 | 500 | 0 | 1.9797 | 2.4172 | 17.617 | 145.9656 | Pump 1 | Pipe 2 | 3684.0206 | 1842839.0037
Pipe 2 | (1031.5975623507745, 1994.7176041834116, 10.0) | (275.5339499512405, 3290.2359614463903, 3.0) | Steel | 20 | 484 | 1500.0163 | -7 | 1900 | 0 | 0 | 2.8686 | 20.4923 | 13.9119 | 132.0537 | Pipe 1 | Pipe 3 | 1140 | 1710018.6199
Pipe 3 | (275.5339499512405, 3290.2359614463903, 3.0) | (100.02140612523948, 2987.4235657956738, 5.0) | PE100-10 | 500 | 440.6 | 350.0057 | 2 | 1900 | 300 | 70 | 3.4616 | 7.5556 | 10.1666 | 121.8871 | Pipe 2 | Pipe 4, Pipe 6 | 1200 | 420006.8571
Pipe 4 | (100.02140612523948, 2987.4235657956738, 5.0) | (-710.8799755422069, 3248.8136112868197, 10.0) | PE100-12.5 | 315 | 268.6 | 852.004 | 5 | 800 | 500 | 20 | 3.9218 | 41.2722 | 47.0564 | 74.8307 | Pipe 3 | Pipe 5 | 640 | 545282.5565
Pipe 5 | (-710.8799755422069, 3248.8136112868197, 10.0) | (-963.7318520066838, 2783.554092127968, 0.0) | Steel | 10 | 253 | 529.623 | -10 | 300 | 300 | 0 | 1.6576 | 5.5826 | -4.2773 | 79.108 | Pipe 4 |  | 520 | 275403.945
Pipe 6 | (100.02140612523948, 2987.4235657956738, 5.0) | (-224.57043511596868, 2427.404145460851, 8.698787951737522) | Steel | 10 | 253 | 647.2985 | 3.6988 | 800 | 300 | 0 | 4.4203 | 41.9633 | 46.6584 | 32.4496 | Pipe 3 | Pipe 7 | 520 | 336595.1989
Pipe 7 | (-224.57043511596868, 2427.404145460851, 8.698787951737522) | (-749.0632077821901, 2530.194204976131, 10.0) | PE100-12.5 | 315 | 268.6 | 534.4718 | 1.3012 | 500 | 500 | 20 | 2.4511 | 10.842 | 12.4496 | 20 | Pipe 6 |  | 640 | 342061.9838
5472208.1649

## Pumps
pump # | center | flow | head | efficiency | start num | power | wetpit min volume | connect to pipe
Pump 1 | (536.08593755699, 1927.8727861776483, -5.0) | 2400 | 163.5826 | 0.75 | 8 | 1425.5565 | 75 | Pipe 1

## eco Pipes
pipe # | start | end | pipe type | nominal dia | id (mm) | length (m) | static head (endZ-startZ) | flow | consumption | minimum pressure required | velocity | head loss | total head loss | Pressure at end of pipe | start with | end with | costs per meter | total costs
Pipe 1 | (536.08593755699, 1927.8727861776483, -5.0) | (1031.5975623507745, 1994.7176041834116, 10.0) | PE100-16 | 800 | 654.8 | 500.2249 | 15 | 2400 | 500 | 0 | 1.9797 | 2.4172 | 17.617 | 76.2423 | Pump 1 | Pipe 2 | 3684.0206 | 1842839.0037
Pipe 2 | (1031.5975623507745, 1994.7176041834116, 10.0) | (275.5339499512405, 3290.2359614463903, 3.0) | Steel | 24 | 582 | 1500.0163 | -7 | 1900 | 0 | 0 | 1.9839 | 8.3486 | 1.5493 | 74.6931 | Pipe 1 | Pipe 3
Pipe 3 | (275.5339499512405, 3290.2359614463903, 3.0) | (100.02140612523948, 2987.4235657956738, 5.0) | PE100-10 | 630 | 555.2 | 350.0057 | 2 | 1900 | 300 | 70 | 2.18 | 2.4507 | 4.6931 | 70 | Pipe 2 | Pipe 4, Pipe 6 | 1760 | 616010.0571
Pipe 4 | (100.02140612523948, 2987.4235657956738, 5.0) | (-710.8799755422069, 3248.8136112868197, 10.0) | PE100-12.5 | 400 | 341.2 | 852.004 | 5 | 800 | 500 | 20 | 2.4304 | 12.8721 | 18.1733 | 51.8267 | Pipe 3 | Pipe 5 | 956 | 814515.8188
Pipe 5 | (-710.8799755422069, 3248.8136112868197, 10.0) | (-963.7318520066838, 2783.554092127968, 0.0) | Steel | 10 | 253 | 529.623 | -10 | 300 | 300 | 0 | 1.6576 | 5.5826 | -4.2773 | 56.104 | Pipe 4 |  | 520 | 275403.945
Pipe 6 | (100.02140612523948, 2987.4235657956738, 5.0) | (-224.57043511596868, 2427.404145460851, 8.698787951737522) | Steel | 16 | 382 | 647.2985 | 3.6988 | 800 | 300 | 0 | 1.939 | 5.6418 | 9.5323 | 46.5717 | Pipe 3 | Pipe 7 | 830 | 537257.7213
Pipe 7 | (-224.57043511596868, 2427.404145460851, 8.698787951737522) | (-749.0632077821901, 2530.194204976131, 10.0) | PE100-12.5 | 315 | 268.6 | 534.4718 | 1.3012 | 500 | 500 | 20 | 2.4511 | 10.842 | 12.4496 | 34.1221 | Pipe 6 |  | 640 | 342061.9838
4428088.5296

## eco Pumps
pump # | center | flow | head | efficiency | start num | power | wetpit min volume | connect to pipe
Pump 1 | (536.08593755699, 1927.8727861776483, -5.0) | 2400 | 93.8593 | 0.75 | 8 | 817.9462 | 75 | Pipe 1

## Channels
channel # | start | end | length (m) | static head (endZ-startZ) | slope | manning coeficent | flow | velocity | water depth | max flow rates | max water depth | geometry: bottom width | geometry: bank slope | geometry: channel depth | geometry: channel width | geometry: free board | start with | end with
Channel 1 | (-271.0696617158046, 4062.033799129046, 10.0) | (-2747.5195659261644, 3116.571339497834, 0.0) | 2650.8118 | 10 | 0.0037724 | 0.035 | 1200 | 0.59094 | 0.29755 |  | 0 | 1 | 3 |  |  | 0.25
Channel 2 | (-2747.5195659261644, 3116.571339497834, 0.0) | (-1565.336305236331, 2430.777475097332, -10.0) | 1366.7372 | 10 | 0.0073167 | 0.035 | 1200 | 0.77767 | 0.37842 | 647.4865 | 0.3 | 0 | 3 |  |  | 0.25
Channel 3 | (-1565.336305236331, 2430.777475097332, -10.0) | (-2357.368366961731, 1234.5574759611845, -20.0) | 1434.6976 | 10 | 0.0069701 | 0.035 | 1200 | 0.7594 | 0.21896 | 10101.8413 | 0.95 | 2 | 0 | 1.2 |  | 0.25