## Pipes
pipe # | start | end | pipe type | nominal dia | id (mm) | length (m) | static head (endZ-startZ) | flow | consumption | minimum pressure required | velocity | head loss | total head loss | Pressure at end of pipe | start with | end with | costs per meter | total costs
Pipe 1 | (536.08593755699, 1927.8727861776483, -5.0) | (1031.5975623507745, 1994.7176041834116, 10.0) | PE100-16 | 800 | 654.8 | 500.2249 | 15 | 2100 | 500 | 0 | 1.7322 | 1.8876 | 17.0406 | 86.1331 | Pump 1 | Pipe 2 | 3684.0206 | 1842839.0037
Pipe 2 | (1031.5975623507745, 1994.7176041834116, 10.0) | (275.5339499512405, 3290.2359614463903, 3.0) | Steel | 20 | 484 | 1500.0163 | -7 | 1600 | 0 | 0 | 2.4157 | 14.9063 | 8.2038 | 77.9293 | Pipe 1 | Pipe 3 | 1140 | 1710018.6199
Pipe 3 | (275.5339499512405, 3290.2359614463903, 3.0) | (100.02140612523948, 2987.4235657956738, 5.0) | PE100-10 | 500 | 440.6 | 350.0057 | 2 | 1600 | 300 | 70 | 2.915 | 5.496 | 7.9293 | 70 | Pipe 2 | Pipe 4, Pipe 6 | 1200 | 420006.8571
Pipe 4 | (100.02140612523948, 2987.4235657956738, 5.0) | (-710.8799755422069, 3248.8136112868197, 10.0) | PE100-12.5 | 315 | 268.6 | 852.004 | 5 | 800 | 500 | 20 | 3.9218 | 41.2722 | 47.0564 | 22.9436 | Pipe 3 | Pipe 5 | 640 | 545282.5565
Pipe 5 | (-710.8799755422069, 3248.8136112868197, 10.0) | (-963.7318520066838, 2783.554092127968, 0.0) | Steel | 10 | 253 | 529.623 | -10 | 300 | 300 | 0 | 1.6576 | 5.5826 | -4.2773 | 27.2208 | Pipe 4 |  | 520 | 275403.945
Pipe 6 | (100.02140612523948, 2987.4235657956738, 5.0) | (-135.58021860004737, 2262.7361389236758, 0.0) | PE100-16 | 315 | 257.8 | 762.04 | -5 | 500 | 300 | 0 | 2.6608 | 18.8783 | 14.2393 | 12.9816 | Pipe 3 | Pipe 7 | 690 | 525807.6139
Pipe 7 | (-135.58021860004737, 2262.7361389236758, 0.0) | (-655.8810770936398, 2220.438554471879, 0.0) | Steel | 8 | 199 | 522.0173 | 0 | 200 | 200 | 0 | 1.7862 | 8.3602 | 8.5229 | 4.4587 | Pipe 6 |  | 445 | 232297.7017

## Pumps
pump # | center | flow | head | efficiency | start num | power | wetpit min volume | connect to pipe
Pump 1 | (536.08593755699, 1927.8727861776483, -5.0) | 2100 | 103.1737 | 0.75 | 8 | 786.7274 | 65.625 | Pipe 1

## eco Pipes
pipe # | start | end | pipe type | nominal dia | id (mm) | length (m) | static head (endZ-startZ) | flow | consumption | minimum pressure required | velocity | head loss | total head loss | Pressure at end of pipe | start with | end with | costs per meter | total costs
Pipe 1 | (536.08593755699, 1927.8727861776483, -5.0) | (1031.5975623507745, 1994.7176041834116, 10.0) | PE100-16 | 710 | 581 | 500.2249 | 15 | 2100 | 500 | 0 | 2.2003 | 3.3792 | 18.6261 | 83.6398 | Pump 1 | Pipe 2 | 2650 | 1325596.1159
Pipe 2 | (1031.5975623507745, 1994.7176041834116, 10.0) | (275.5339499512405, 3290.2359614463903, 3.0) | Steel | 20 | 484 | 1500.0163 | -7 | 1600 | 0 | 0 | 2.4157 | 14.9063 | 8.2038 | 75.4359 | Pipe 1 | Pipe 3 | 1140 | 1710018.6199
Pipe 3 | (275.5339499512405, 3290.2359614463903, 3.0) | (100.02140612523948, 2987.4235657956738, 5.0) | PE100-10 | 560 | 493.6 | 350.0057 | 2 | 1600 | 300 | 70 | 2.3226 | 3.1609 | 5.4359 | 70 | Pipe 2 | Pipe 4, Pipe 6 | 1440 | 504008.2285
Pipe 4 | (100.02140612523948, 2987.4235657956738, 5.0) | (-710.8799755422069, 3248.8136112868197, 10.0) | PE100-12.5 | 400 | 341.2 | 852.004 | 5 | 800 | 500 | 20 | 2.4304 | 12.8721 | 18.1733 | 51.8267 | Pipe 3 | Pipe 5 | 956 | 814515.8188
Pipe 5 | (-710.8799755422069, 3248.8136112868197, 10.0) | (-963.7318520066838, 2783.554092127968, 0.0) | Steel | 10 | 253 | 529.623 | -10 | 300 | 300 | 0 | 1.6576 | 5.5826 | -4.2773 | 56.104 | Pipe 4 |  | 520 | 275403.945
Pipe 6 | (100.02140612523948, 2987.4235657956738, 5.0) | (-135.58021860004737, 2262.7361389236758, 0.0) | PE100-16 | 355 | 290.6 | 762.04 | -5 | 500 | 300 | 0 | 2.094 | 10.5356 | 5.7592 | 50.3448 | Pipe 3 | Pipe 7 | 850 | 647734.0171
Pipe 7 | (-135.58021860004737, 2262.7361389236758, 0.0) | (-655.8810770936398, 2220.438554471879, 0.0) | Steel | 8 | 199 | 522.0173 | 0 | 200 | 200 | 0 | 1.7862 | 8.3602 | 8.5229 | 41.8219 | Pipe 6 |  | 445 | 232297.7017

## eco Pumps
pump # | center | flow | head | efficiency | start num | power | wetpit min volume | connect to pipe
Pump 1 | (536.08593755699, 1927.8727861776483, -5.0) | 2100 | 102.2658 | 0.75 | 8 | 779.8048 | 65.625 | Pipe 1

## Channels
channel # | start | end | length (m) | static head (endZ-startZ) | slope | manning coeficent | flow | velocity | water depth | max flow rates | max water depth | geometry: bottom width | geometry: bank slope | geometry: channel depth | geometry: channel width | geometry: free board | start with | end with
Channel 1 | (-271.0696617158046, 4062.033799129046, 10.0) | (-2747.5195659261644, 3116.571339497834, 0.0) | 2650.8118 | 10 | 0.0037724 | 0.035 | 1200 | 0.59094 | 0.29755 |  | 0 | 1 | 3 |  |  | 0.25
Channel 2 | (-2747.5195659261644, 3116.571339497834, 0.0) | (-1565.336305236331, 2430.777475097332, -10.0) | 1366.7372 | 10 | 0.0073167 | 0.035 | 1200 | 0.77767 | 0.37842 | 647.4865 | 0.3 | 0 | 3 |  |  | 0.25
Channel 3 | (-1565.336305236331, 2430.777475097332, -10.0) | (-2357.368366961731, 1234.5574759611845, -20.0) | 1434.6976 | 10 | 0.0069701 | 0.035 | 1200 | 0.7594 | 0.21896 | 10101.8413 | 0.95 | 2 | 0 | 1.2 |  | 0.25