## Pipes
pipe # | start | end | pipe type | nominal dia | id (mm) | length (m) | static head (endZ-startZ) | flow | consumption | minimum pressure required | velocity | head loss | total head loss | Pressure at end of pipe | start with | end with | costs per meter | total costs
Pipe 1 | (536.08593755699, 1927.8727861776483, -5.0) | (1031.5975623507745, 1994.7176041834116, 10.0) | PE100-16 | 800 | 654.8 | 500.2249 | 15 | 1600 | 500 | 0 | 1.3198 | 1.1407 | 16.2296 | 75.5386 | Pump 1 | Pipe 2 | 3684.0206 | 1842839.0037
Pipe 2 | (1031.5975623507745, 1994.7176041834116, 10.0) | (275.5339499512405, 3290.2359614463903, 3.0) | Steel | 20 | 484 | 1500.0163 | -7 | 1100 | 0 | 0 | 1.6608 | 7.4473 | 0.58792 | 74.9506 | Pipe 1 | Pipe 3 | 1140 | 1710018.6199
Pipe 3 | (275.5339499512405, 3290.2359614463903, 3.0) | (100.02140612523948, 2987.4235657956738, 5.0) | PE100-10 | 500 | 440.6 | 350.0057 | 2 | 1100 | 300 | 70 | 2.0041 | 2.7459 | 4.9506 | 70 | Pipe 2 | Pipe 4 | 1200 | 420006.8571
Pipe 4 | (100.02140612523948, 2987.4235657956738, 5.0) | (-710.8799755422069, 3248.8136112868197, 10.0) | PE100-12.5 | 315 | 268.6 | 852.004 | 5 | 800 | 500 | 20 | 3.9218 | 41.2722 | 47.0564 | 22.9436 | Pipe 3 | Pipe 5 | 640 | 545282.5565
Pipe 5 | (-710.8799755422069, 3248.8136112868197, 10.0) | (-963.7318520066838, 2783.554092127968, 0.0) | Steel | 10 | 253 | 529.623 | -10 | 300 | 300 | 0 | 1.6576 | 5.5826 | -4.2773 | 27.2208 | Pipe 4 |  | 520 | 275403.945

## Pumps
pump # | center | flow | head | efficiency | start num | power | wetpit min volume | connect to pipe
Pump 1 | (536.08593755699, 1927.8727861776483, -5.0) | 1600 | 91.7681 | 0.75 | 8 | 533.1481 | 50 | Pipe 1

## eco Pipes
pipe # | start | end | pipe type | nominal dia | id (mm) | length (m) | static head (endZ-startZ) | flow | consumption | minimum pressure required | velocity | head loss | total head loss | Pressure at end of pipe | start with | end with | costs per meter | total costs
Pipe 1 | (536.08593755699, 1927.8727861776483, -5.0) | (1031.5975623507745, 1994.7176041834116, 10.0) | PE100-16 | 630 | 515.6 | 500.2249 | 15 | 1600 | 500 | 0 | 2.1286 | 3.6532 | 18.8842 | 82.9235 | Pump 1 | Pipe 2 | 2280 | 1140512.8846
Pipe 2 | (1031.5975623507745, 1994.7176041834116, 10.0) | (275.5339499512405, 3290.2359614463903, 3.0) | Steel | 18 | 433 | 1500.0163 | -7 | 1100 | 0 | 0 | 2.075 | 12.8085 | 6.0281 | 76.8954 | Pipe 1 | Pipe 3 | 870 | 1305014.2099
Pipe 3 | (275.5339499512405, 3290.2359614463903, 3.0) | (100.02140612523948, 2987.4235657956738, 5.0) | PE100-10 | 450 | 396.6 | 350.0057 | 2 | 1100 | 300 | 70 | 2.4734 | 4.5835 | 6.8954 | 70 | Pipe 2 | Pipe 4 | 1010 | 353505.7714
Pipe 4 | (100.02140612523948, 2987.4235657956738, 5.0) | (-710.8799755422069, 3248.8136112868197, 10.0) | PE100-12.5 | 400 | 341.2 | 852.004 | 5 | 800 | 500 | 20 | 2.4304 | 12.8721 | 18.1733 | 51.8267 | Pipe 3 | Pipe 5 | 956 | 814515.8188
Pipe 5 | (-710.8799755422069, 3248.8136112868197, 10.0) | (-963.7318520066838, 2783.554092127968, 0.0) | Steel | 10 | 253 | 529.623 | -10 | 300 | 300 | 0 | 1.6576 | 5.5826 | -4.2773 | 56.104 | Pipe 4 |  | 520 | 275403.945

## eco Pumps
pump # | center | flow | head | efficiency | start num | power | wetpit min volume | connect to pipe
Pump 1 | (536.08593755699, 1927.8727861776483, -5.0) | 1600 | 101.8077 | 0.75 | 8 | 591.4754 | 50 | Pipe 1

## Channels
channel # | start | end | length (m) | static head (endZ-startZ) | slope | manning coeficent | flow | velocity | water depth | max flow rates | max water depth | geometry: bottom width | geometry: bank slope | geometry: channel depth | geometry: channel width | geometry: free board | start with | end with
Channel 1 | (-271.0696617158046, 4062.033799129046, 10.0) | (-2747.5195659261644, 3116.571339497834, 0.0) | 2650.8118 | 10 | 0.0037724 | 0.035 | 1200 | 0.59094 | 0.29755 |  | 0 | 1 | 3 |  |  | 0.25
Channel 2 | (-2747.5195659261644, 3116.571339497834, 0.0) | (-1565.336305236331, 2430.777475097332, -10.0) | 1366.7372 | 10 | 0.0073167 | 0.035 | 1200 | 0.77767 | 0.37842 | 647.4865 | 0.3 | 0 | 3 |  |  | 0.25
Channel 3 | (-1565.336305236331, 2430.777475097332, -10.0) | (-2357.368366961731, 1234.5574759611845, -20.0) | 1434.6976 | 10 | 0.0069701 | 0.035 | 1200 | 0.7594 | 0.21896 | 10101.8413 | 0.95 | 2 | 0 | 1.2 |  | 0.25